# Fire Door Inspection Report

SYNTHETIC DEMO DATA — NOT A REAL INSPECTION OR ENGINEERING DECISION

Purpose. This fictional report is designed only for Inspectra demonstrations. It contains multiple explicit findings so extraction, classification, review priority, and evidence highlighting can be demonstrated safely.

# Inspection summary

| Field | Value |
| --- | --- |
| Report ID | SYN-FD-2026-001 |
| Site | Demo Residence Block C |
| Asset | Level 03 corridor fire door FD-C-03-17 |
| Inspection date | 10 September 2026 |
| Inspection type | Routine functional and visual inspection |
| Overall disposition | Corrective work required before routine closeout |

# Scope and method

Visual examination, door operation test, latch engagement check, frame-gap measurement, seal condition check, and hardware review were performed. No certification assessment was performed.

# Findings

| ID | Component or location | Observed condition | Priority | Recommended action |
| --- | --- | --- | --- | --- |
| FD-01 | Hinge-side frame | Frame gap measures 7 mm over approximately 420 mm at mid-height. | High | Adjust frame or leaf alignment; remeasure after repair. |
| FD-02 | Door closer | Door closes with excessive speed and rebounds before latch engagement. | High | Adjust closer speed and latch action; perform ten-cycle test. |
| FD-03 | Bottom seal | Intumescent and smoke seal is detached for approximately 180 mm at the lower edge. | Medium | Replace damaged seal and verify continuous adhesion. |
| FD-04 | Latch strike plate | One strike-plate fixing screw is missing and the plate is loose. | Medium | Install compatible fixing screw and verify latch engagement. |
| FD-05 | External leaf face | Two dents and surface scratches are visible near the pull handle. | Low | Repair finish where required; confirm no effect on operation. |

# Inspector narrative

The door leaf opened freely but closed too quickly under closer force. On three of ten cycles, the leaf rebounded and the latch did not fully engage without manual assistance.

A 7 mm clearance was measured between the hinge-side leaf and frame at mid-height. The bottom smoke seal was partly detached and a loose strike plate was observed. Cosmetic dents and scratches were also present on the external face.

# Disposition

The door should remain in the corrective-action queue. Reinspect the closer, latch, frame gap, and seal after repairs. This synthetic report does not determine fire-door compliance.

# Corrective action closeout

| Finding | Assigned role | Target date | Closeout status |
| --- | --- | --- | --- |
| FD-01 | Maintenance owner | 17 September 2026 | Open — verification required |
| FD-02 | Maintenance owner | 17 September 2026 | Open — verification required |
| FD-03 | Maintenance owner | 17 September 2026 | Open — verification required |
| FD-04 | Maintenance owner | 17 September 2026 | Open — verification required |
| FD-05 | Maintenance owner | 17 September 2026 | Open — verification required |

Inspector declaration. All information in this document is fictional and intended exclusively for software demonstration and testing.